Idea: compare two fans to understand the h_eff at low and high RPMs;

We’d like to arrive at an efficiency curve like this for any fan:

Pick: 2 fans to arrive at nominal power efficiencies of the design RPM (16k vs 32.5k RPM):

Fan 1 (high speed): https://www.delta-fan.com/pfb0412en-e.html

Fan 2 (lower speed): https://www.delta-fan.com/pfb0412ehn-tp06.html

Using this tool, we extract two PQ curves, one from each fan datasheet

https://plotdigitizer.com/app

Next, we use the datasheet to determine the max and min voltages/currents, interpolate these ranges to identify the various operating powers which correspond to the CFM and P values from the curve. We then estimate P_total at any given CFM point.

Then we take the extracted PQ curve, estimate the P_cool for each CFM, and construct an efficiency curve for both fans. These are shown below:

| Model | PFB0412 | PFB0412-tp06 |
| --- | --- | --- |
| RPM | 32500 | 16000 |
| Q(CFM) | 22.24 | 11.67 |
| P(mmH2O) | 96.57 | 15.14 |
| V | 12.20 | 12.01 |
| I | 3.10 | 0.55 |
| P_cool | 9.940125 | 0.817333194 |
| P_tot | 37.82 | 6.564217911 |
| eta | 0.262827 | 0.124513416 |
| V_max | 13.2 | 13.2 |
| V_min | 10.8 | 10.8 |
| I_max | 3.5 | 0.6 |
| I_min | 2.6 | 0.5 |

Using the above table,

Now, we go to the CFD simulation to help us estimate the h_eff curve. Ideally, we’d sweep over all CFMs for a given fan, but this is unrealistic because any real fan chosen for a server would be chosen based on the optimal

Nominal efficiency (12.4%), 16000 RPM: hotspot temp is 34C, ambient is 19.85

Nominal efficiency (26.2%), 32500 RPM: hotspot temp is xxC, ambient is 19.85:

NOTES:

https://hvacknowitall.com/blog/the-3-fan-laws-and-fan-curve-charts

## Fan Law 1: CFM is directly proportional to RPM.

## Fan Law 2: Total Static Pressure changes with the square of CFM (or RPM).

## Fan Law 3: Horsepower changes with the cube of CFM (or RPM)